## PDU
family | TYPE | BASIC DESC. | MODEL | DESCRIPTION
PDU | EPDUBAS1 | EASY BASIC 11KW | EPDU1216B | Easy PDU, Basic, Zero U, 11 kW, 230V, (36) C13 & (6) C19；IEC309
PDU | EPDUBAS2 | EASY BASIC 22KW | EPDU1232B | Easy PDU, Basic, Zero U, 22 kW, 230V, (30) C13 & (12) C19；IEC309
PDU | EPDUBAS3 | EASY BASIC 3,5KW | EPDU1116B | Easy PDU,Basic,ZeroU,16A,230V,(20)C13 & (4)C19; IEC309
PDU | EPDUBAS7 | EASY BASIC 7KW | EPDU1132B | Easy PDU, Basic, Zero U, 32A, 230V, (20)C13 & (4)C19；IEC309
PDU | EPDUMET1 | EASY METERED 11KW | EPDU1216M | Easy PDU, Metered, Zero U, 11 kW, 230V, (21) C13 & (3) C19;IEC309
PDU | EPDUMET2 | EASY METERED 22KW | EPDU1232M | Easy PDU, Metered, Zero U, 22 kW, 230V, (18) C13 & (6) C19;IEC309
PDU | EPDUMET3 | EASY METERED 3,5KW | EPDU1116M | Easy PDU,Metered,ZeroU,16A,230V,(18)C13 & (3)C19; IEC309
PDU | EPDUMET7 | EASY METERED 7KW | EPDU1132M | Easy PDU, Metered, Zero U, 32A, 230V, (20)C13 & (4)C19；IEC309
PDU | EPDUSWI3 | EASY SWITCHED 3,5KW | EPDU1116S | Easy PDU, Switched,ZeroU,16A,230V,(20)C13 & (4)C19, IEC309
PDU | EPDUSWI7 | EASY SWITCHED 7KW | EPDU1132S | Easy PDU, Switched, Zero U, 32A, 230V, (20)C13 & (4)C19;IEC309
PDU | PDUBAS1 | BASIC 11KW | AP7557 | Rack PDU, Basic, Zero U, 11 kW, 230V, (36) C13 & (6) C19
PDU | PDUBAS2 | BASIC 22KW | AP7555A | Rack PDU, Basic, Zero U, 22kW, 230V, (6) C19 & (3) C13
PDU | PDUBAS3 | BASIC 3,5KW | AP7551 | Rack PDU, Basic, ZeroU, 16A, 230V, (20)C13 & (4)C19; IEC309
PDU | PDUBAS7 | BASIC 7KW | AP7553 | Rack PDU, Basic, Zero U, 32A, 230V, (20)C13 & (4)C19
PDU | PDUMET1 | METERED 11KW | AP8881 | Rack PDU 2G, Metered, ZeroU, 11kW, 230V, (36) C13 & (6) C19
PDU | PDUMET2 | METERED 22KW | AP8886 | Rack PDU 2G, Metered, ZeroU, 22.0kW(32A) 17.3kW(24A), 230V, (30) C13 & (12) C19
PDU | PDUMET3 | METERED 3,5KW | AP8858EU3 | Rack PDU 2G, Metered, ZeroU, 16A, 230V, (18) C13 & (2) C19, IEC309 Cord
PDU | PDUMET7 | METERED 7KW | AP8853 | Rack PDU 2G, Metered, ZeroU, 32A, 230V, (36) C13 & (6) C19
PDU | PDUSWI1 | SWITCHED 11KW | APDU9981EU3 | Rack PDU 9000 Switched, ZeroU, 11.0kW, 230V, (21) C13 & (3) C19
PDU | PDUSWI3 | SWITCHED 3,5KW | AP8959 | Rack PDU 2G, Switched, ZeroU, 16A/230V, (21) C13 & (3) C19
PDU | PDUSWI7 | SWITCHED 7KW | AP8953 | Rack PDU 2G, Switched, ZeroU, 32A, 230V, (21) C13 & (3) C19

## RackDetails
type | HEIGHT | WIDTH | DEPTH | Inrow | Overhead | Inrow | Overhead
AR2480 | 42 | 800 | 1060 | 1 | 1 | 1 | 1
AR2487 | 48 | 800 | 1060 | 1 | 0 | 1 | 1
AR2580 | 42 | 800 | 1200 | 2 | 2 | 1 | 1
AR2587 | 48 | 800 | 1200 | 2 | 0 | 1 | 1
AR3100 | 42 | 600 | 1070 | 1 | 1 | 1 | 1
AR3107 | 48 | 600 | 1070 | 1 | 0 | 1 | 1
AR3150 | 42 | 750 | 1070 | 1 | 1 | 1 | 1
AR3157 | 48 | 750 | 1070 | 1 | 0 | 1 | 1
AR3300 | 42 | 600 | 1200 | 2 | 2 | 1 | 1
AR3307 | 48 | 600 | 1200 | 2 | 0 | 1 | 1
AR3350 | 42 | 750 | 1200 | 2 | 2 | 1 | 1
AR3357 | 48 | 750 | 1200 | 2 | 0 | 1 | 1

## NoUPS
NO UPS
| 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
KW | 155 | 249 | 392 | 623 | 500 | 700 | 800 | 900 | 1000 | 2000
KVA
ELECTRICAL PANEL | 250 | 400 | 630 | 1000 | NA | NA | NA | NA | NA | NA

## Rack
RACK_AR2480 | Netshelter SV 42U 800mm x 1060mm
RACK_AR2487 | NetShelter SV 48U 800mm x 1060mm
RACK_AR2580 | NetShelter SV 42U 800mm x 1200mm
RACK_AR2587 | NetShelter SV 48U 800mm x 1200mm
RACK_AR3100 | NetShelter SX 42U 600mm x 1070mm
RACK_AR3107 | NetShelter SX 48U 600mm Wide x 1070mm
RACK_AR3150 | NetShelter SX 42U 750mm Wide x 1070mm
RACK_AR3157 | NetShelter SX 48U 750mm Wide x 1070mm
RACK_AR3300 | NetShelter SX 42U/600mm/1200mm
RACK_AR3307 | NetShelter SX 48U 600mm x 1200mm
RACK_AR3350 | NetShelter SX 42U 1200 x 750
RACK_AR3357 | NetShelter SX 48U 750mm x 1200mm

## UPS
SYMMETRA
| 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1
KW | 16 | 32 | 48 | 64 | 80 | 96 | 112 | 128 | 144 | 160
KVA | 16 | 32 | 48 | 64 | 80 | 96 | 112 | 128 | 144 | 160
FAMILY | SYMMETRA PX | SYMMETRA PX | SYMMETRA PX | SYMMETRA PX | SYMMETRA PX | SYMMETRA PX | SYMMETRA PX | SYMMETRA PX | SYMMETRA PX | SYMMETRA PX
DESCRIPTION | SYMMETRA PX 16KW | SYMMETRA PX 32KW | SYMMETRA PX 48KW | SYMMETRA PX 64KW | SYMMETRA PX 80KW | SYMMETRA PX 96KW | SYMMETRA PX 112KW | SYMMETRA PX 128KW | SYMMETRA PX 144KW | SYMMETRA PX 160KW
P/N ASSY | SY16K48H-PD | SY32K48H-PD | SY48K48H-PD | SY64K96H | SY80K96H | SY96K160H | SY112K160H | SY128K160H | SY144K160H | SY160K160H
SKU | SY16K48H-PD | SY32K48H-PD | SY48K48H-PD | SY64K96H | SY80K96H | SY96K160H | SY112K160H | SY128K160H | SY144K160H | SY160K160H
ELECTRICAL PANEL | 250 | 250 | 250 | 400 | 400 | 400 | 400 | 630 | 630 | 630
Width | 600 | 600 | 600 | 1200 | 1200 | 1200 | 1800 | 1800 | 1800 | 1800
Depth | 1070 | 1070 | 1070 | 1070 | 1070 | 1070 | 1070 | 1070 | 1070 | 1070
LAYOUT | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Type | 48H | 48H | 48H | 96H | 96H | 96H | 160H | 160H | 160H | 160H
GALAXY VS/VM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1
KW | 15 | 20 | 20 | 30 | 30 | 40 | 40 | 50 | 50 | 60 | 60 | 80 | 80 | 100 | 100 | 120 | 150 | 144 | 180
KVA | 15 | 20 | 20 | 30 | 30 | 40 | 40 | 50 | 50 | 60 | 60 | 80 | 80 | 100 | 100 | 120 | 150 | 160 | 200
FAMILY | GALAXY VS | GALAXY VS | GALAXY VSN+1 | GALAXY VS | GALAXY VSN+1 | GALAXY VS | GALAXY VSN+1 | GALAXY VS | GALAXY VSN+1 | GALAXY VS | GALAXY VSN+1 | GALAXY VS | GALAXY VSN+1 | GALAXY VS | GALAXY VSN+1 | GALAXY VS | GALAXY VS | GALAXY VM | GALAXY VM
DESCRIPTION | GALAXY VS 15 | GALAXY VS 20 | GALAXY VSN+1 20 | GALAXY VS 30 | GALAXY VSN+1 30 | GALAXY VS 40 | GALAXY VSN+1 40 | GALAXY VS 50 | GALAXY VSN+1 50 | GALAXY VS 60 | GALAXY VSN+1 60 | GALAXY VS 80 | GALAXY VSN+1 80 | GALAXY VS 100 | GALAXY VSN+1 100 | GALAXY VS 120 | GALAXY VS 150 | GALAXY VM 160 | GALAXY VM 200
P/N ASSY | GVS_15 | GVS_20 | GVSN+1_20 | GVS_30 | GVSN+1_30 | GVS_40 | GVSN+1_40 | GVS_50 | GVSN+1_50 | GVS_60 | GVSN+1_60 | GVS_80 | GVSN+1_80 | GVS_100 | GVSN+1_100 | GVS_120 | GVS_150 | GXYVM_160 | GXYVM_200
SKU | GVSUPS15KB2HS | GVSUPS20KB2HS | GVSUPS20KR0B5HS | GVSUPS30KB4HS | GVSUPS30KR0B5HS | GVSUPS40KB4HS | GVSUPS40KR0B5HS | GVSUPS50KB4HS | GVSUPS50KR0B5HS | GVSUPS60K0B5HS | GVSUPS60KRHS | GVSUPS80K0B5HS | GVSUPS80KRHS | GVSUPS100KHS | GVSUPS100KRHS | GVSUPS120KHS | GVSUPS150KHS | GVMPB160KHS | GVMPB200KHS
ELECTRICAL PANEL | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 400 | 400 | 400 | 400 | 400 | 4000 | 630 | 630 | 630 | 630
WIDTH | 521 | 521 | 521 | 521 | 521 | 521 | 521 | 521 | 521 | 521 | 521 | 521 | 521 | 1071 | 521 | 521 | 521 | 1052 | 1052
DEPTH | 847 | 847 | 847 | 847 | 847 | 847 | 847 | 847 | 847 | 847 | 847 | 847 | 847 | 847 | 847 | 847 | 847 | 854 | 854
LAYOUT | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 1 | 4 | 4 | 4 | 2 | 2
RUNTIME (min) | 12.5 | 8.5 |  | 6.1 |  | 7.3 |  | 5.2 |  | 6.2 |  | 5.6 |  | 5.2 |  | 5.9 | 5.9
| 7Ah (VRLA) | 7Ah (VRLA) |  | 9Ah (VRLA) |  | 9Ah (VRLA) |  | 9Ah (VRLA) |  | 9Ah (VRLA) |  | 9Ah (VRLA) |  | 9Ah (VRLA)
EASY UPS
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2
KW | 10 | 15 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 160 | 200
KVA | 10 | 15 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 160 | 200
FAMILY | Easy UPS 3S | Easy UPS 3S | Easy UPS 3S | Easy UPS 3S | Easy UPS 3S | Easy UPS 3M | Easy UPS 3M | Easy UPS 3M | Easy UPS 3M | Easy UPS 3M | Easy UPS 3M
DESCRIPTION | Easy UPS 3S 10 | Easy UPS 3S 15 | Easy UPS 3S 20 | Easy UPS 3S 30 | Easy UPS 3S 40 | Easy UPS 3M 60 | Easy UPS 3M 80 | Easy UPS 3M 100 | Easy UPS 3M 120 | Easy UPS 3M 160 | Easy UPS 3M 200
P/N ASSY | E3S_10 | E3S_15 | E3S_20 | E3S_30 | E3S_40 | E3M_60 | E3M_80 | E3M_100 | E3M_120 | E3M_160 | E3M_200
SKU | E3SUPS10KHB1 | E3SUPS15KHB2 | E3SUPS20KHB1 | E3SUPS30KHB1 | E3SUPS40KHB1 | E3MUPS60KHB1S | E3MUPS80KHB1S | E3MUPS100KHS | E3MUPS120KHS | E3MUPS160KHS | E3MUPS200KHS
ELECTRICAL PANEL | 250 | 250 | 250 | 250 | 250 | 400 | 400 | 400 | 400 | 630 | 630
WIDTH | 380 | 380 | 380 | 500 | 500 | 360 | 360 | 360 | 500 | 500 | 600
DEPTH | 928 | 928 | 928 | 969 | 969 | 850 | 850 | 850 | 850 | 850 | 850
LAYOUT | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 4 | 3 | 5
RUNTIME (min) | 10.5 | 5.9 | 10.5 | 6 | 7.1 | 6 | 5.4 | 7.5 | 5.4 | 6.9 | 7.4
| E3SBTH4 | E3SBTH4 | E3SBTH4 | E3SBTH4 | E3SBTH4 |  |  | E3MCBC10A | E3MCBC10A | 2xE3MCBC7B | 2XE3MCBC10A

## ContainerUPS
ACRC301S | INROW3CW | 1 | 300 | 22.1 | 11 | 11 | 22 | 22 | 22
ACRC602 | INROW6CW | 2 | 600 | 39.7 | 11 | 11 | 22 | 22 | 22
ACRD602P | INROW9DX | 3 | 600 | 33.2 | 11 | 11 | 22 | 22 | 22
UCA 0481 | UNISPLIT | 4 | 0 | 15.7 | 11 | 11 | 22 | 22 | 22
WMF0661 | WALLMOUNT1 | 5 | 0 | 16 | 11 | 11 | 22 | 22 | 22
- | - | 6 | 0 | 29 | 11 | 11 | 22 | 22 | 22
ACRD602 | INROW6DX | 7 | 600 | 28 | 11 | 11 | 22 | 22 | 22
ACRD301S | INROW3DX | 8 | 300 | 24.4 | 11 | 11 | 22 | 22 | 22
ACRC602P | INROW6PCW | 9 | 600 | 39.7 | 11 | 11 | 22 | 22 | 22
ACRD301P | INROW3PDX | 10 | 300 | 24.4 | 11 | 11 | 22 | 22 | 22
LDAV | CRAC1DX | 11 | PHYSICAL CONSTRAINT - MODULE SPACE & COOLING |  | 7.3 | 7.3 | 7.3 | 7.3 | 7.3
LDCV | CRAH1CW | 12 |  | LENGHT | 7.3 | 7.3 | 7.3 | 7.3 | 7.3
ISO20' | LAYOUT_01 | N | ISO20' LAYOUT_01 N | 4532 | 4532 | 4532 | 4532 | 4532 | 4532 | 4532 | 4532 | 4532 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 0 | 0
ISO20' | LAYOUT_01 | 2N | ISO20' LAYOUT_01 2N | 3980 | 3980 | 3980 | 3980 | 3980 | 3980 | 3980 | 3980 | 3980 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 0 | 0
ISO20' | LAYOUT_02 | N | ISO20' LAYOUT_02 N | 3832 | 3832 | 3832 | 3832 | 3832 | 3832 | 3832 | 3832 | 3832 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 0 | 0
ISO20' | LAYOUT_02 | 2N | ISO20' LAYOUT_02 2N | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 0 | 0
ISO20' | LAYOUT_03 | N | ISO20' LAYOUT_03 N | 2804 | 2804 | 2804 | 3004 | 3004 | 2804 | 2804 | 2804 | 2804 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 0 | 0
ISO20' | LAYOUT_03 | 2N | ISO20' LAYOUT_03 2N | 1904 | 1904 | 1904 | 1704 | 1704 | 1904 | 1904 | 1904 | 1904 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 0 | 0
ISO20' | LAYOUT_04 | N | ISO20' LAYOUT_04 N | 3394 | 3394 | 3394 | 3394 | 3394 | 3394 | 3394 | 3394 | 3394 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 0 | 0
ISO20' | LAYOUT_04 | 2N | ISO20' LAYOUT_04 2N | 2394 | 2394 | 2394 | 2129 | 2129 | 2394 | 2394 | 2394 | 2394 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 0 | 0
ISO20' | LAYOUT_05 | N | ISO20' LAYOUT_05 N | 2204 | 2204 | 2204 | 2204 | 2204 | 2204 | 2204 | 2204 | 2204 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 0 | 0
ISO20' | LAYOUT_05 | 2N | ISO20' LAYOUT_05 2N | 1604 | 1604 | 1604 | 1604 | 1604 | 1604 | 1604 | 1604 | 1604 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 0 | 0
ISO40' | LAYOUT_01 | N | ISO40' LAYOUT_01 N | 10330 | 10330 | 10330 | 10330 | 10330 | 10330 | 10330 | 10330 | 10330 | 0 | 0 | 0 | 0 | 0 | 8 | 7 | 0 | 0 | 0 | 0 | 0
ISO40' | LAYOUT_01 | 2N | ISO40' LAYOUT_01 2N | 9220 | 9220 | 9220 | 9220 | 9220 | 9220 | 9220 | 9220 | 9220 | 0 | 0 | 0 | 0 | 0 | 8 | 7 | 0 | 0 | 0 | 0 | 0
ISO40' | LAYOUT_02 | N | ISO40' LAYOUT_02 N | 9790 | 9790 | 9790 | 9790 | 9790 | 9790 | 9790 | 9790 | 9790 | 0 | 0 | 0 | 0 | 0 | 8 | 7 | 0 | 0 | 0 | 0 | 0
ISO40' | LAYOUT_02 | 2N | ISO40' LAYOUT_02 2N | 8725 | 8725 | 8725 | 8500 | 8500 | 8725 | 8725 | 8725 | 8725 | 0 | 0 | 0 | 0 | 0 | 8 | 7 | 0 | 0 | 0 | 0 | 0
ISO40' | LAYOUT_03 | N | ISO40' LAYOUT_03 N | 8900 | 8900 | 8900 | 9100 | 9100 | 8900 | 8900 | 8900 | 8900 | 0 | 0 | 0 | 0 | 0 | 8 | 7 | 0 | 0 | 0 | 0 | 0
ISO40' | LAYOUT_03 | 2N | ISO40' LAYOUT_03 2N | 8000 | 8000 | 8000 | 7800 | 7800 | 8000 | 8000 | 8000 | 8000 | 0 | 0 | 0 | 0 | 0 | 8 | 7 | 0 | 0 | 0 | 0 | 0
ISO40' | LAYOUT_04 | N | ISO40' LAYOUT_04 N | 9490 | 9490 | 9490 | 9490 | 9490 | 9490 | 9490 | 9490 | 9490 | 0 | 0 | 0 | 0 | 0 | 8 | 7 | 0 | 0 | 0 | 0 | 0
ISO40' | LAYOUT_04 | 2N | ISO40' LAYOUT_04 2N | 8490 | 8490 | 8490 | 8225 | 8225 | 8490 | 8490 | 8490 | 8490 | 0 | 0 | 0 | 0 | 0 | 8 | 7 | 0 | 0 | 0 | 0 | 0
ISO40' | LAYOUT_05 | N | ISO40' LAYOUT_05 N | 8300 | 8300 | 8300 | 8300 | 8300 | 8300 | 8300 | 8300 | 8300 | 0 | 0 | 0 | 0 | 0 | 8 | 7 | 0 | 0 | 0 | 0 | 0
ISO40' | LAYOUT_05 | 2N | ISO40' LAYOUT_05 2N | 7700 | 7700 | 7700 | 7700 | 7700 | 7700 | 7700 | 7700 | 7700 | 0 | 0 | 0 | 0 | 0 | 8 | 7 | 0 | 0 | 0 | 0 | 0
NON ISO25' | LAYOUT_01 | N | NON ISO25' LAYOUT_01 N | 6129 | 6129 | 6129 | 5864 | 5864 | 6129 | 6129 | 6129 | 6129 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 0 | 0 | 0 | 0 | 0
NON ISO25' | LAYOUT_01 | 2N | NON ISO25' LAYOUT_01 2N | 5864 | 5864 | 5864 | 5864 | 5864 | 5864 | 5864 | 5864 | 5864 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 0 | 0 | 0 | 0 | 0
NON ISO25' | LAYOUT_02 | N | NON ISO25' LAYOUT_02 N | 5864 | 5864 | 5864 | 5864 | 5864 | 5864 | 5864 | 5864 | 5864 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 0 | 0 | 0 | 0 | 0
NON ISO25' | LAYOUT_02 | 2N | NON ISO25' LAYOUT_02 2N | 4854 | 4854 | 4854 | 4624 | 4624 | 4854 | 4854 | 4854 | 4854 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 0 | 0 | 0 | 0 | 0
NON ISO25' | LAYOUT_03 | N | NON ISO25' LAYOUT_03 N | 5744 | 5744 | 5744 | 5744 | 5744 | 5744 | 5744 | 5744 | 5744 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 0 | 0 | 0 | 0 | 0
NON ISO25' | LAYOUT_03 | 2N | NON ISO25' LAYOUT_03 2N | 4254 | 4254 | 4254 | 3629 | 3629 | 4254 | 4254 | 4254 | 4254 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 0 | 0 | 0 | 0 | 0
NON ISO25' | LAYOUT_04 | N | NON ISO25' LAYOUT_04 N | 5679 | 5679 | 5679 | 5679 | 5679 | 5679 | 5679 | 5679 | 5679 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 0 | 0 | 0 | 0 | 0
NON ISO25' | LAYOUT_04 | 2N | NON ISO25' LAYOUT_04 2N | 4129 | 4129 | 4129 | 4129 | 4129 | 4129 | 4129 | 4129 | 4129 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 0 | 0 | 0 | 0 | 0
NON ISO25' | LAYOUT_05 | N | NON ISO25' LAYOUT_05 N | 4834 | 4834 | 4834 | 4589 | 4589 | 4834 | 4834 | 4834 | 4834 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 0 | 0 | 0 | 0 | 0
NON ISO25' | LAYOUT_05 | 2N | NON ISO25' LAYOUT_05 2N | 3164 | 3164 | 3164 | 2924 | 2924 | 3164 | 3164 | 3164 | 3164 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 0 | 0 | 0 | 0 | 0
NON ISO45' | LAYOUT_01 | N | NON ISO45' LAYOUT_01 N | 12225 | 12225 | 12225 | 11960 | 11960 | 12225 | 12225 | 12225 | 12225 | 0 | 0 | 0 | 0 | 0 | 9 | 8 | 0 | 0 | 0 | 0 | 0
NON ISO45' | LAYOUT_01 | 2N | NON ISO45' LAYOUT_01 2N | 11960 | 11960 | 11960 | 11960 | 11960 | 11960 | 11960 | 11960 | 11960 | 0 | 0 | 0 | 0 | 0 | 9 | 8 | 0 | 0 | 0 | 0 | 0
NON ISO45' | LAYOUT_02 | N | NON ISO45' LAYOUT_02 N | 11960 | 11960 | 11960 | 11960 | 11960 | 11960 | 11960 | 11960 | 11960 | 0 | 0 | 0 | 0 | 0 | 9 | 8 | 0 | 0 | 0 | 0 | 0
NON ISO45' | LAYOUT_02 | 2N | NON ISO45' LAYOUT_02 2N | 10950 | 10950 | 10950 | 10720 | 10720 | 10950 | 10950 | 10950 | 10950 | 0 | 0 | 0 | 0 | 0 | 9 | 8 | 0 | 0 | 0 | 0 | 0
NON ISO45' | LAYOUT_03 | N | NON ISO45' LAYOUT_03 N | 11840 | 11840 | 11840 | 11840 | 11840 | 11840 | 11840 | 11840 | 11840 | 0 | 0 | 0 | 0 | 0 | 9 | 8 | 0 | 0 | 0 | 0 | 0
NON ISO45' | LAYOUT_03 | 2N | NON ISO45' LAYOUT_03 2N | 10350 | 10350 | 10350 | 9725 | 9725 | 10350 | 10350 | 10350 | 10350 | 0 | 0 | 0 | 0 | 0 | 9 | 8 | 0 | 0 | 0 | 0 | 0
NON ISO45' | LAYOUT_04 | N | NON ISO45' LAYOUT_04 N | 11775 | 11775 | 11775 | 11775 | 11775 | 11775 | 11775 | 11775 | 11775 | 0 | 0 | 0 | 0 | 0 | 9 | 8 | 0 | 0 | 0 | 0 | 0
NON ISO45' | LAYOUT_04 | 2N | NON ISO45' LAYOUT_04 2N | 10225 | 10225 | 10225 | 10225 | 10225 | 10225 | 10225 | 10225 | 10225 | 0 | 0 | 0 | 0 | 0 | 9 | 8 | 0 | 0 | 0 | 0 | 0
NON ISO45' | LAYOUT_05 | N | NON ISO45' LAYOUT_05 N | 10930 | 10930 | 10930 | 10685 | 10685 | 10930 | 10930 | 10930 | 10930 | 0 | 0 | 0 | 0 | 0 | 9 | 8 | 0 | 0 | 0 | 0 | 0
NON ISO45' | LAYOUT_05 | 2N | NON ISO45' LAYOUT_05 2N | 9260 | 9260 | 9260 | 9020 | 9020 | 9260 | 9260 | 9260 | 9260 | 0 | 0 | 0 | 0 | 0 | 9 | 8 | 0 | 0 | 0 | 0 | 0
NON ISO25' | LAYOUT_01 | N | NON ISO25' LAYOUT_01 N | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 6120 | 6120 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 0 | 0 | 3082 | 3082 | 0 | 0
NON ISO25' | LAYOUT_01 | 2N | NON ISO25' LAYOUT_01 2N | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 6120 | 6120 | 0 | 0 | 0 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 3320 | 3320 | 1074 | 1106
NON ISO25' | LAYOUT_02 | N | NON ISO25' LAYOUT_02 N | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 6120 | 6120 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 0 | 0 | 3082 | 3082 | 0 | 0
NON ISO25' | LAYOUT_02 | 2N | NON ISO25' LAYOUT_02 2N | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 6120 | 6120 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 0 | 0 | 2725 | 2725 | 1106 | 1106
NON ISO25' | LAYOUT_03 | N | NON ISO25' LAYOUT_03 N | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 6120 | 6120 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 0 | 0 | 3082 | 3082 | 0 | 0
NON ISO25' | LAYOUT_03 | 2N | NON ISO25' LAYOUT_03 2N | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 6120 | 6120 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 0 | 0 | 2725 | 2725 | 1106 | 1106
NON ISO25' | LAYOUT_04 | N | NON ISO25' LAYOUT_04 N | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 6120 | 6120 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 0 | 0 | 1036 | 1036 | 0 | 0
NON ISO25' | LAYOUT_04 | 2N | NON ISO25' LAYOUT_04 2N | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 6120 | 6120 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 0 | 0 | 2013 | 2013 | 0 | 0
NON ISO25' | LAYOUT_05 | N | NON ISO25' LAYOUT_05 N | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 6120 | 6120 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 0 | 0 | 1036 | 1036 | 0 | 0
NON ISO25' | LAYOUT_05 | 2N | NON ISO25' LAYOUT_05 2N | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 5400 | 6120 | 6120 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 0 | 0 | 2013 | 2013 | 0 | 0
NON ISO45' | LAYOUT_01 | N | NON ISO45' LAYOUT_01 N | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 12260 | 12260 | 0 | 0 | 0 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 3082 | 3082 | 0 | 0
NON ISO45' | LAYOUT_01 | 2N | NON ISO45' LAYOUT_01 2N | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 12260 | 12260 | 0 | 0 | 0 | 20 | 12 | 0 | 0 | 0 | 0 | 0 | 3320 | 3320 | 1106 | 1106
NON ISO45' | LAYOUT_02 | N | NON ISO45' LAYOUT_02 N | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 12260 | 12260 | 0 | 0 | 0 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 3082 | 3082 | 0 | 0
NON ISO45' | LAYOUT_02 | 2N | NON ISO45' LAYOUT_02 2N | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 12260 | 12260 | 0 | 0 | 0 | 20 | 12 | 0 | 0 | 0 | 0 | 0 | 2725 | 2725 | 1106 | 1106
NON ISO45' | LAYOUT_03 | N | NON ISO45' LAYOUT_03 N | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 12260 | 12260 | 0 | 0 | 0 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 3082 | 3082 | 0 | 0
NON ISO45' | LAYOUT_03 | 2N | NON ISO45' LAYOUT_03 2N | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 12260 | 12260 | 0 | 0 | 0 | 20 | 12 | 0 | 0 | 0 | 0 | 0 | 2725 | 2725 | 1106 | 1106
NON ISO45' | LAYOUT_04 | N | NON ISO45' LAYOUT_04 N | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 12260 | 12260 | 0 | 0 | 0 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 1036 | 1036 | 0 | 0
NON ISO45' | LAYOUT_04 | 2N | NON ISO45' LAYOUT_04 2N | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 12260 | 12260 | 0 | 0 | 0 | 20 | 12 | 0 | 0 | 0 | 0 | 0 | 2013 | 2013 | 0 | 0
NON ISO45' | LAYOUT_05 | N | NON ISO45' LAYOUT_05 N | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 12260 | 12260 | 0 | 0 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 1036 | 1036 | 0 | 0
NON ISO45' | LAYOUT_05 | 2N | NON ISO45' LAYOUT_05 2N | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 11500 | 12260 | 12260 | 0 | 0 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 2013 | 2013 | 0 | 0

## ERVAndARS
ERV / ARS
ISO20' | ARS_ISO | ISO20'ARS_ISO | 1
ISO20'_ETO | ARS_ISO | ISO20'_ETOARS_ISO | 1
ISO40' | ARS_ISO | ISO40'ARS_ISO | 2
ISO40'_ETO | ARS_ISO | ISO40'_ETOARS_ISO | 2
NON ISO25' | ARS_NONISO | NON ISO25'ARS_NONISO | 2
NON ISO45' | ARS_NONISO | NON ISO45'ARS_NONISO | 2
NON ISOD45 | ARS_NONISO | NON ISOD45ARS_NONISO | 3

## CRACoolingType
CRAH DX |  | LDAV
| 3 | 3 | 2 | 2
KW | 87.4 | 93.6 | 99.6 | 135
MODEL | 2422A | 2522A | 2722A | 3822A
LENGTH | 2082 | 2650 | 2650 | 2650
COST
CRAH CW |  | LDCV
| 4 | 3 | 3 | 3 | 2 | 2 | 2
KW | 37.7 | 54.2 | 75.4 | 89.6 | 121 | 129.9 | 144
MODEL | 0800A | 1400A | 1800A | 2500A | 3400A | 4000A | 4300A
LENGTH | 1010 | 1310 | 1720 | 2170 | 2582 | 2582 | 2582
COST